## Sheet1
Schools Planned Building Maintenance Checklist
** Please note this list is not exhaustive**
Key: Red = Statutory requirements
Item | Frequency | Responsibility | Date last checked | Date last checked | Date last checked | Comments
Air Conditioning
Checking/testing/servicing | Half yearly or annually dependent on usage | School
Air conditioning energy performance certificate which can be | 5 years apart. | School
Energy Certificates (for more info contact Laser)
If building > 1000m2 Display Energy Certificate (DEC) | Every year and an Advisory Report every 7 years | School
Between 250m2 and 1000m2 needs a DEC and Advisory Report (AR) | Every 10 years | School
An Energy Performance Certificate (EPC) | Should be issued when a school is constructed, sold or leased. | School
Asbestos
Premises Inspection | 3 yearly | KCC
Schools have mandatory responsibilities. Please refer to the schools asbestos report for details as well as KCC's policy and guidance. | Refer to guidance | School
Automatic Doors
Servicing | Annually as a minimum refer to manfuacturer's guidance | School
Drains, Gullies and Drainage Channels
Clear drains, gullies and drainage channels including soakaways | Annually (Autumn time this may revert to monthly to clear excess leaves etc) | School
Electrical Inspection
Inspection and testing hard wiring | 5 yearly | KCC
Resultant works C1 and C2 | refer to report | KCC
Other resultant works | refer to report | School
Emergency Lighting
Testing | Quarterly | KCC
General walk round - basic visual inspection | Weekly | School
Testing of selected fittings, on/off only | Monthly | School
1 hour drain down of lighting (turn off electric supply to check battery) record in log book | 1st Quarter | School
2 hour drain down of lighting (turn off electric supply to check battery) record in log book | 2nd Quarter | School
1 hour drain down of lighting (turn off electric supply to check battery) record in log book | 3rd Quarter | School
2 hour drain down of lighting (turn off electric supply to check battery) record in log book | 4th Quarter | School
Fire Alarm
Full Testing | 6 monthly | KCC
Test on call point, different call point each time, record in log book. | Weekly | School
Fire Risk Assessment
Fire Risk Assessment | One of but keep updated | School
Fire Management Plan | One of but keep updated | School
Glazing
Glazing maintenance eg ensure safety filmed areas are in good condition. | Annually (safety film has a 10 - 15 year lifespan) | School
Gutters and Roofs
Clear out. Remove debris and flush through with a hosepipe. | Annually as a minimum dependent on site location. (Autumn time this may revert to monthly to clear excess leaves etc) | School
Roofs , clean off. Remove debris and foreign bodies | Annually as a minimum dependent on site location. | School
Heating - Electric Convector Heaters
Clean | Annually | School
Heating - Gas
Boilers and plant tested inspected and serviced | Annually | KCC
Gas Carcass certification tested | 3 yearly | KCC
Radiators/Heating | Turn on and test prior to heating season | School
Heating - Liquid Propane Gas (LPG)
Tank and pipework inspection by competent person | Annually | KCC
Visual checks (compound secure, vegetation controlled, check for damage) see LPG risk assessment for relevant items. | 3 times a year | School
Heating - Oil
Boilers and plant tested inspected and serviced | 6 monthly | KCC
Oil certification tested | Annually | KCC
Radiators/Heating | Turn on and test prior to heating season | School
Check oil supply | Prior to heating season | School
Intruder Alarm/CCTV
Servicing and Testing | Annually | School
Kitchens
Gas supply to kitchen | 6 monthly | KCC
Extract system | Annually - as minimum | School
Gas catering equipment | Annually | KCC
Lifts
Servicing and Testing of passenger lifts, step lifts, ….. | Dependent on lift model, manufacturer's recommendations, could range from monthly quarterly or six monthly as a minimum
Mobile Hoists | As per manufacturers instructions | School
Lightening Protection
Inspection and testing | Annually | School
Playgrounds and other external areas
Inspection of external areas to ensure physical damp proof ie barrier to prevent damp entering a building is not breached. | 5 yearly | School
Check surface of play areas to ensure no trip hazards | Annually | School
Playground equipment | Regularly | School
Portable Appliance Testing (PAT)
PAT Testing - generally | Annually | School
Items containing elements eg tea, urn, kettle | 6 monthly | School
Sprinklers
Pump Test | Weekly | School
Servicing | Quarterly | School
Trees
Safety Inspection (visual) | Annually but dependent on red, amber or green zone | KCC
Resultant works from survey, ie tree removal or work to tree | As per report recommendations | School
Water Hygiene Checks
Risk Assessment | Every 2 years | KCC
Risk Assessment Review – Every 2 years in-between the Risk Assessment | Every 2 years | KCC
Monthly temperature monitoring | Monthly | School
Weekly flushing of low used outlets | Weekly | School
Quarterly clean and disinfection of showers | Quarterly | School
Biannual and annual tank inspections | Every 2 years | School
Monitoring of systems | As required by Risk Assessment | School
Swimming Pools | Daily - or as advised in water hygiene risk assessment | School
Hydrotherapy Pools | Daily - or as advised in water hygiene risk assessment | School
Windows
Maintenance of moving parts of PVCu and aluminium | Annually | School
Preserving treatment of wooden windows and cladding | As required on annual inspection by school | School
Maintain/redecorate timber joinery to prevent deterioration | 5 - 10 years | School
Useful information - www.kent.gov.uk
For more advice please contact building maintenance enquiries email buildmaintenq@kent.gov.uk